# MaxAir HVAC Setup Guide

MaxAir will initially be configured as a WiFi AP (Access Point) named MaxAirHotspot, connect to the AP using the password **1234567890** and browse to IP address **192.168.50.5** where you will be presented with the initial connection screen.

Select your local WiFi SSID from the dropdown list and enter the associated password.

Alternatively, if you want MaxAir to operated as a ‘stand-alone’ AP, just click to select AP Mode.

Finally click on ‘Set and Restart.

If working in AP Mode you will be presented with the MaxAir login screen, otherwise reconnect to your local AP and browse to the IP address associated with MaxAir (if your AP is using DHCP, then access your router to determine which IP address has been allocated).


The system can be accessed from a suitable WEB browser using its IP address on the local network. The system can be configured with both a wireless and/or an Ethernet wired connection.

The default login credentials are username – **admin** and password - **pihome**


## System Modes

The MaxAir system has two ***system modes***:


1. HVAC – MaxAir is configured to control heating, ventilation and air conditioning installations, where three switching relays are required. Multi Zone operation is also supported, through the use of additional zone control relays.
2. Boiler - MaxAir is configured to control heating systems where a boiler and zone relays are used, typically switching relays will be required for the boiler and each zone.



The system mode by selecting ‘System Configuration’ from the Settings dropdown list, then clicking the ‘Mode’ button.




The Mode button on the Home page can operate either as a cyclic button, scrolling through each mode of operation or can be used to open a pop-up menu, which allows selection of the desired operating mode.

Click on the ‘Mode’ button then select the system mode from the dropdown list and click on the ‘Save’ button to update the system.

## Operating Modes – HVAC Configuration, Cyclic Operation

When configured to operate in ‘HVAC Mode’, the MaxAir system has eight operating modes:



The system is disable.

The system is operating in Heating Timer Mode, with on/off timings and temperatures controlled by schedules, but with no cooling capability.

The system is operating in Cooling Timer Mode, with on/off timings and temperatures controlled by schedules, but with no heating capability.

The system is operating in Auto Timer Mode, with on/off timings controlled by schedules and with the temperature controlled by the Zone Default Temperature, switching between heating and cooling as required.

The HVAC zone operates continually with the temperature controlled by the Zone Default Temperature, switching between heating and cooling as required.


The fan operates continually.


The HVAC zone operates continually with the temperature controlled by the Zone Default Temperature but with no cooling capability.

The HVAC zone operates continually with the temperature controlled by the Zone Default Temperature but with no heating capability.

## Operating Modes – Button Operation


The operating modes are the same as above. The Home screen button is of a slightly different format:

The Mode button shows the currently selected operating mode in the legend at the top of the button, clicking on the button will open a popup menu showing the available options.

When the system is configured to work in HVAC mode, the selection screen reflects the available HVAC operating modes.

## Example Configuration – Single Zone Mode

The example will configure the system to operate in HVAC mode with a single zone providing the temperature control. An additional ‘stand-alone’ temperature sensor located in the Main Bedroom is also configured



Before use the system must be configured to match the local system to be controlled.

## Configuration

The system configuration follows a four-layer model: -

|  |
| --- |
| **Schedules** |
| **Zones** |
| **Devices** |
| **Nodes** |

Each layer is built from the previous layer e.g. Devices are built using Nodes and Schedules are built using Zones.

### Nodes

The nodes are the basic hardware devices that control the system. Some nodes are auto‑detected, others must be defined manually.

Examples of auto‑detected nodes are MySensors temperature sensors and MySensors relay modules, while examples of manually defined devices are GPIO connected relays, I2C relay modules, Tasmota type switches and MQTT sensors/controlleers.

### Devices

Devices define how the system recognises the nodes hardware, devices are either Temperature Sensors or Relays. The devices are defined manually.

### Zones

For HVAC systems a single zone will be created to control the heating, colling and fan components. Further zones can be added for example to control Tasmota switch/s.

### Schedules

Schedules are time related definitions which dictate when the system performs actions and the parameters associated with those actions. An example would be a schedule to control the hot water zone, with a start time 0f 0600 hours, a stop time of 0930 hours and a maximum temperature of 40°C.


The system to be configured comprises the following elements:


1. A HVAC system requiring 3 controller relays
2. A MySensors Temperature to control the HVAC system.
3. A MySensors Temperature to measure a bedroom temperature

The above will determine the MaxAir nodes requirements as follows:

1. Two MySensors Temperature Sensors
2. Three GPIO pins for relays
3. A serial or WiFi gateway device to send/receive messages to/from 1 and 2

### Step 1 – Configure the Gateway





The gateway is configured by selecting ‘Node and Zone Configuration’ from the Settings dropdown list, then clicking the ‘Gateway’ button.


For this example, a MySensor gateway is required and should be configured as either Serial or WiFi.

If no MySensors gateway is required eg where both sensors and relays are connected to the GPIO port or when MQTT devices are used, then configure as a Virtual gateway (this is the initial default configuration).



Once the gateway has been configured, the script file which executes the task on a regular time interval will be executed by the ‘Job Scheduler’, which is configured by default. It can be accessed by selecting ‘System Configuration’ from the Settings dropdown list, then clicking the ‘Jobs’ button.





A listing of the scheduled jobs will be displayed. New Jobs can be added or the settings for existing Jobs modified or deleted.

### Step 2 – Layer 1 Configuration - Connect the Nodes

### Step 2 – Layer 1 Configuration - Connect the Nodes


Once the gateway is running, connect the MySensors Temperature Sensor devices, so that they can be detected.



To show the nodes currently available, select ‘Node and Zone Configuration’ from the Settings dropdown list, then

The example configuration uses relays connected via GPIO pins, the GPIO node is created by default as part of the initial setup process.

The Nodes menu option will show the default GPIO node plus the 2 autodetected MySensor nodes.



**This completes the Layer 1 configuration.**


### Step 3 – Layer 2 Configuration - Add Devices

This step will add the Relay and Temperature Sensor devices.

#### Relays

The example system will require 3 HVAC control relays.




 Select Device Configuration from the Settings dropdown list, then click the ‘Relay’ button.to display a list of any currently configured relays.



Click on the ‘Add Relay’ button to configure the first relay



An alternative method to go directly to the Add Relay dialogue, is from the Home screen click on the ‘One Touch’ button then select the ‘Add Relay’ menu item.

Select the Controller Type e.g. HVAC - Heat


Provide a name for this relay device

Select the Relay ID from the dropdown list of available Nodes

Choose the Child ID from the dropdown list, in the case of a GPIO controller, this will be a GPIO pin.

Select the level to trigger the relay ON.

Click on ‘Submit’ to add the device.

Repeat the process to add the two further Controller relays.


Re-selecting the Relays menu item from the Settings/Node and Zone Configuration menu will display the updated list of currently configured relays.


This dialogue can be used to Add/Delete/Edit the relay configurations.

### Temperature Sensors

The example system will use 3 temperature sensors, one for the Central Heating, one for the Hot Water and a third to monitor a bedroom temperature. The configuration process is very similar to that used to configure the relay devices.




 To display a list of any currently configured sensors, select ‘Device Configuration’ from the Settings dropdown list, then click the ‘Sensors’ button.



Click on the ‘Add Sensor’ button to configure the first sensor



An alternative method to go directly to the Add Sensor dialogue, is from the Home screen click on the ‘One Touch’ button then select the ‘Add Sensor’ menu item.



Show either before or after the system controller on the Home screen

Used to order where on the Home screen the sensor is displayed

Either Temperature or Humidity

Provide a name for this sensor device

Select the Sensor ID from the dropdown list of available Nodes

Choose the Child ID from the dropdown list, nodes with only 1 sensor, this will be 0

Select either Continuous date reporting or only on-change of data.

For on-change mode, the maximum time between reporting data, in minutes.


Positive or Negative factor to be applied to the sensor reading as a correction.

Select the frost protection temperature or 0 to disable this feature

If frost protection is enabled, then select the zone to be activated on protection

Click on ‘Submit’ to add the device.

Repeat the process to add any other temperature sensors.

Re-selecting the Sensors menu item from the Settings/Node and Zone Configuration menu will display the updated list of currently configured temperature sensors.


This dialogue can be used to Add/Delete/Edit the sensor configurations.

The ‘Show’ tickbox can be used suppress displaying a sensor on the Home screen, with the exception of any sensors allocated to a zone.


This example shows one unallocated and two allocated sensors.

#### System Controller Configuration

Three relays are used to activate the heating, cooling and fan functions of the HVAC system, these relays were added as a relay devices above and now need to be associated with the ‘system Controller’.



Select ‘System Controller Configuration’ from the Settings dropdown list, then click the ‘SC’ button.



Enter a name for this controller

Select the HEATING relay from the dropdown list

Select the COOLING relay from the dropdown list

Select the FAN relay from the dropdown list

Enter a hysteresis value in minutes

Enter a maximum running time in minutes


Click on ‘Save’ to update

**This completes the Layer 2 configuration.**

**Layers 1 and 2 define the basic hardware configuration of the system.**

### Step 4 – Layer 3 Configuration - Add Zones

The example configuration has a single zone to control the HVAC system.

To display a list of any currently configured sensors, select ‘Node and Zone Configuration’ from the Settings dropdown list, then click the ‘Zones’ button.




Click on the ‘Add Zone’ button to configure the first zone.




An alternative method to go directly to the Add Zone dialogue, is from the Home screen click on the ‘One Touch’ button then select the ‘Add Zone’ menu item.

There are currently eight types of zone, Heating, Water, Immersion, Switch, HVAC, HVAC-M, Humidity and Binary. The format of the Add Zone dialogue will depend on the type of zone selected, for example Immersion type zones will disable ‘System Controller’ selection, while Switch type zones will disable all temperature sensor related selections, together with the ‘System Controller’ selection, as these parameters do not apply to these zone types.

The example below shows a typical HVAC zone configuration. Once the parameters have been entered, click on the ‘Submit’ button.






Re-selecting the Zone menu item from the Settings/Node and Zone Configuration menu will display the updated list of currently configured zones.

This dialogue can be used to Add/Delete/Edit the zone configurations.

**This completes the Layer 3 configuration.**

### Step 5 – Layer 4 Configuration - Add Schedules

The example configuration will have a single schedule to control the Central Heating and Hot Water zones.


Click on the toolbar clock icon to configure the first schedule.



Click on + or ‘Add Schedule’

The Add schedule screen will be presented, the example below shows:

* An enabled schedule
* Operated Monday to Friday
* Titled Weekdays AM
* Operated between 0630 hours and 0930 hours
* Uses 19°C as the Target temperature




Once configured, click on the ‘Submit’ button to add the schedule.


Add any other schedules as required.

**This completes the Layer 4 configuration.**


### Step 6 – Scheduled Jobs

In order for the system to function a number of tasks need to operate at pre-determined time intervals. These tasks are configured as part of the initial setup process.



 To show the list of active tasks, select ‘System Configuration’ from the Settings dropdown list, then click the ‘Jobs’ button.

The default configuration is as shown and for example, as can be seen the ‘check\_ds18b20’ is not enabled, this job is only required if 1-Wire temperature sensors are connected to the GPIO bus.





New scheduled tasks can be added by clicking on the ‘Add Job’ button.


**THIS COMPLETES THE BASIC SETUP**

**The Single Zone configuration is available as an example database at:**

**/var/www/MySQL\_Database/hvac\_example\_231121.sql**

## Example Configuration – Multi Zone Mode

The difference between Single Zone and Multi Zone modes is that ‘Zone Controller’ relays are required to control the operation of individual zones, for example by activating and deactivating ‘Dampers’ on a zone-by-zone basis. Control for the individual zones will be through the use of temperature sensors allocated to each zones.



The changes to the previous Single Zone example will be:

### Layer 1 Configuration

Add additional sensor and controller nodes as required to support each zone.

### Layer 2 Configuration


Create Sensor and Relay devices as required to support each zone.

### Layer 3 Configuration

Multiple Zones will be created depending on the configuration of the HVAC system. The difference in the case of Multi Zone is that the ‘Zone Controller’ selection box will be available, so that one or more zone controller relay can be associated with the zone.

The example below shows the configuration for ‘HVAC Zone1’, with its associated Sensor and Controller.

This process would be repeated for any additional zones, using the relevant Sensor and Controller.



### Layer 4 Configuration

Schedules would be created for the individual zones as required.